# Treatment failure in the QMRA tool: approach and decisions

Text for the main part of the report (draft, 2026-10-17)

# 1	Purpose

A quantitative microbial risk assessment (QMRA) usually assumes that every treatment step always reaches its log removal value (LRV). In practice, treatment steps sometimes fail: a UV lamp breaks, a filter is bypassed, a dosing pump stops. Short failures can contribute a large part of the annual infection risk, because a few days with poorly treated water can outweigh many days of normal operation.

The QMRA tool was therefore extended so that each treatment step can be given failure events. This chapter explains the idea of the approach and the reasons behind its main decisions. The equations and the full algorithm are given in the annex. The approach builds on the failure approach of Hambsch et al. (2019) and departs from it in the points explained below.

# 2	Starting point: the QMRA tool without failures

The tool estimates the annual probability of infection and the disease burden (DALYs) for three reference pathogens (Rotavirus, Campylobacter jejuni and Cryptosporidium parvum). It runs a Monte Carlo simulation: for each simulated year, it draws the pathogen concentration in the source water for every exposure event of the year, reduces it by the LRV of the treatment train, and turns the ingested dose into a probability of infection.

The uncertainty about the treatment performance is expressed by two cases. Best-case uses the maximum LRV of every treatment step, worst-case uses the minimum LRV. The range between the two cases shows how much the result depends on the treatment performance.

# 3	Failure inputs

Each treatment step has three failure inputs. They apply to all pathogen groups of the step.

- Failure frequency: the expected number of failure days per year (0 to 365). With the default of 0, the step never fails.

- Failure duration: the average length of one failure event in minutes (1 to 1,440, default 30).

- Number of parallel units: how many equal units share the water of the step (a whole number of 1 or more, default 1).

The inputs were chosen because operators know them or can estimate them from their operating records: on how many days a year something goes wrong, for how long, and how the step is built.

# 4	Main ideas and the reasons for them

## 4.1	Failure days are drawn at random for each exposure event

The tool builds the annual risk from exposure events, not from calendar days. For drinking water there is one exposure event per day, but for other uses there are far fewer, for example 20 irrigation events per year. For each exposure event, the tool therefore draws at random whether it falls on a failure day of a treatment step, with a probability that follows from the failure frequency. Each treatment step is drawn independently.

Why: the source method counts 365 days per year. That only fits exposures with one event per day. Drawing per exposure event works for every exposure, uses one calculation for one or several failing steps, and fits the existing simulation. As a consequence, the number of failure events varies between simulated years, as it does in reality. This widens the range of annual risks.

## 4.2	A failure event stops one of the parallel units

Many treatment steps consist of several parallel units, for example several UV reactors or filters. A failure event is assumed to stop one of these units while the others keep working. The water of the stopped unit passes untreated, the rest is treated as usual. A step with one unit therefore loses its whole LRV during a failure. A step with two units keeps a small LRV, because only half of the water is untreated.

Why: in most cases a treatment step does not lose all its removal during a failure. A first idea, one reduction percentage for all pathogen groups, was dropped, because the same percentage for viruses, bacteria and protozoa has no physical meaning. The number of parallel units describes how the step is built, and the remaining LRV follows from it for each pathogen group.

An important property follows from this: the untreated share limits what the step can achieve during a failure. A step with two units keeps at most about 0.3 log, however high its normal LRV is, and a step with ten units at most 1 log. Parallel units therefore help, but they do not replace a working barrier.

## 4.3	The failure duration counts in both cases

The water used on a failure day is assumed to be a mixture of water treated during the failure and water treated in normal operation, in proportion to the failure duration (the mixed-water assumption). A failure of 4 hours, for example, affects one sixth of the water of that day. For each failing step, this gives a daily LRV that lies between its LRV during the failure and its normal LRV.

Best-case and worst-case use the same rule. They differ only in the LRV a step starts from, its maximum or minimum LRV, as in normal operation.

Why: an earlier version assumed in worst-case that all water used on a failure day had been treated during the failure, so the duration had no effect in worst-case. Consistently, best-case would then have to assume that the water was never treated during the failure, and neither case would depend on the duration. That is not plausible. The duration is better read as the probability that water used on a failure day was treated during the failure: the longer the failure, the more likely this is. Using the same rule in both cases keeps the range between best-case and worst-case a measure of the treatment performance only.

## 4.4	Water is mixed by concentration, not by LRV

The daily LRV is calculated from the mixed pathogen concentrations, not as an average of the LRVs over the day.

Why: LRVs are logarithms. A small share of untreated water dominates the mixture, so an average of the LRVs is far too optimistic. In the example below, it would give a failing UV disinfection a daily LRV of 2.5 instead of 0.78.

## 4.5	Combined failures add up without further rules

If several treatment steps fail on the same day, each failing step gets its own daily LRV, and the daily LRVs of all steps are added up. This is the same as if each failure happened at a random time of the day, independently of the other steps.

Why: the alternative, arranging failures within the day so that they overlap as little or as much as possible, would need extra rules, for example for failures that add up to more than one day. Treating the failures as independent avoids these rules and gives results between the two extremes.

## 4.6	Only positive LRVs are affected

A failure removes only the positive LRVs of a step. An LRV of 0 or below, which can be used to describe recontamination, stays unchanged.

# 5	Assumptions and limitations

- Independent failures. Failure days of different treatment steps are independent. Common causes, such as a power failure that stops several steps, are not modelled.

- Units failing together. Parallel units that fail together, for example through a shared power supply, are not modelled. Such a step should be entered with one unit.

- Average concentration over the day. The daily LRV uses the average concentration of the water used on a failure day. This is slightly more conservative than drawing for each exposure event whether it falls inside the failure.

- Default duration. With the default failure duration of 30 minutes, worst-case results are much less conservative than with a full loss for the whole day. The failure duration should therefore be set from operating experience.

- Draft. The approach and this text are to be reviewed by a domain expert before the release of the tool.

# 6	Example

The example shows the effect of a failing UV disinfection on the infection risk from Cryptosporidium parvum in drinking water (365 exposure events per year, 1 L per event). The source water contains 0.1 to 10 oocysts per litre. The treatment train has two steps: a filtration with a protozoa LRV of 2 to 3 and a UV disinfection with a protozoa LRV of 2.5 to 3. The values are illustrative and are not the default values of the tool. Only the UV disinfection fails, on 10 days per year. The results were calculated with the tool.

Median annual probability of infection with Cryptosporidium parvum. The tolerable risk level is 10-4 infections per person per year.

| UV failure (10 days per year) | Best-case | Worst-case |
| --- | --- | --- |
| No failures | 4.0 × 10-5 | 1.3 × 10-3 |
| 60 minutes, 1 unit | 8.1 × 10-5 | 1.7 × 10-3 |
| 60 minutes, 2 units | 6.1 × 10-5 | 1.5 × 10-3 |
| 4 hours, 1 unit | 2.0 × 10-4 | 2.9 × 10-3 |
| 4 hours, 2 units | 1.2 × 10-4 | 2.1 × 10-3 |
| 24 hours, 1 unit | 1.0 × 10-3 | 1.1 × 10-2 |

Without failures, best-case lies below the tolerable risk level of 10-4 per year. Ten failure days of one hour double the best-case risk. With failures of four hours, best-case exceeds the tolerable risk level by a factor of two; a second UV unit reduces this to just above the level. A failure of a whole day on ten days per year raises the best-case risk about 25-fold. Worst-case already exceeds the tolerable risk level without failures, and failures raise it further.

The example also shows why the water is mixed by concentration. On a failure day with a 4-hour failure, the UV disinfection (LRV 3, one unit) reaches a daily LRV of 0.78. An average of the LRVs over the day would give 2.5, which would hide most of the effect of the failure.

# 7	Differences from the source method

The approach follows Hambsch et al. (2019) in its main idea: failure days with a reduced LRV, and the mixed-water assumption with the failure duration. It departs from it in three points:

- Failure days are drawn per exposure event instead of counting 365 days per year.

- Worst-case uses the failure duration in the same way as best-case. In the source, worst-case removes the LRV of the failing step for the whole day.

- The number of parallel units is new: in the source, a failing step always loses its whole LRV.

# 8	Reference

Hambsch, B., Lipp, P., Ho, J. (2019): Modelhafte Prüfung und Konzeptentwicklung zur quantitativen Risikobewertung der mikrobiellen Rohwasserbelastung für die Trinkwasseraufbereitung (Abschlussbericht). DVGW-Förderkennzeichen W 201808. Technologiezentrum Wasser, Karlsruhe.